| AUTO EMS / MPS HEATER ERROR CODES |  |
| --- | --- |
| Error 30 FAN_LIMP | No fan speed signal received for 200 sec. [3min 20 sec] |
| Error 31 RoLL_TERR | Flame detected on burner after gas valve has closed |
| Error 32 DATA_Err | Malfunction or failure of NG-Lo module |
| Error 35 No_SA-THM | S/A Thermistor not detected or open circuit |
| Error 36 BAdSA-THM | S/A Thermistor not reached 33 deg within 2 min |
| Error 37 TACHO-Err | No RPM signal received or signal greater that 1500 RPM |
| Error 40 OHEAT_R-A | Overheat of R/A klixon |
| Error 41 OHEAT_S-A | S/A overheat switch open |
| Error 42 OHEAT_THM | S/A Thermistor exceeded 90 deg |
| Error 43 OHCooLDwn | Result of error 40, 41 or 42 |
| Error 44 RoLLOuT | Flame sensed on Afro sensing rod |
| Error 45 LOW24VOLT | Low power supply, resulting in insufficient 24 VAC output |
| Error 46 IGN_RETRY | re-ignition attempt when burner did not light within 5 sec |
| Error 50 IGN_LKOUT | Ignition lockout after 4 ignition attempts & burner did not light |
| Error 51 FLMS_LOSS | Pilot flame loss before main burner started |
| Error 52 FLM_NOGAS | Flame detected on burner without valve being energised |
| Error 53 OH_LKOUT | Unit had 2 over temperature conditions within 13 mins |
| Error 54 RoL_LKOUT | Unit locked out after 3 consecutive flame roll out (3 x Err 44) |
| Error 55 IGNINVALID | Flame lost within 10 sec of valve opening 6 consecutive times |
| Error 56 PowER_UPD | Power interruption |
| Error 60 MOTOR_O-C | Main fan motor open circuit |
| Error 61 503_FAIL1 | Malfunction or failure of NG-Lo module |
| Error 62 HSI_LOCK | HIS ignitor is open circuit |
| Error 63 503_FAIL5 | Malfunction or failure of NG-Lo module |
| Error 64 503_FAIL | Malfunction or failure of NG-Lo module |
| Error 65 MTR_LKOUT | Main fan motor open circuit and no speed sensor signal |
| Error 67 503_WD | Malfunction or failure of NG-Lo module |
| Error 68 503 nCCFG_Err | Malfunction or failure of NG-Lo module |
| Error 69 FUSE_BLOW | Blown fuse or lower that 24 VAC output of transformer |
| Error 70 FSAFE_LOC | Flame loss on backup flame sensor |
| Error 71 FSaFE_LOC | Flame loss on backup flame sensor |