| STARPRO HEATER ERROR CODES |  |  |
| --- | --- | --- |
| 30 | Fan Limp | No fan speed signal received for 200 sec. [3min 20 sec] |
| 32 | Data Error | Board Failure |
| 33 | MDGU_Limp | Feedback current not detected from Gas Valve |
| 35 | No_SA_THM | S/A Thermistor not detected or open circuit |
| 36 | BAdSA-THM | S/A Thermistor not reached 33 deg within 2 min |
| 40 | OHEAT_R-A | Combustion fan O/H switch open |
| 41 | OHEAT_S-A | S/A overheat switch open |
| 42 | OHEAT_THM | S/A Thermistor exceeded 90 deg |
| 43 | OHCoolDwn | Result of error 40, 41 or 42 |
| 44 | RoLLOut | Result of error 40, 41 or 42 |
| 45 | LOW24VOLT | Result of error 40, 41 or 42 |
| 46 | IGR_NOFLM | Flame lost at burner during ignition |
| 47 | IGR_BDFLM | Flame lost during flame prove state |
| 48 | LOST_PRES | Combustion Chamber Pressure switch open |
| 49 | LOST_FLME | Unexpected flame loss during heating cycle |
| 50 | IGN_LKOUT | No gas flue or Ignition, Afro rollout detected |
| 51 | RLT_NOGAS | No gas flue or Ignition, Afro rollout detected |
| 52 | FLM_NOGAS | Flame picked up, but valve not open |
| 53 | OH_LKOUT | Number of O/H Cool downs events exceeded 2 |
| 54 | RoL_LKOUT | Duriing ignition, flame detected on Afro |
| 55 | IGNVALID | After max number of ignition attempts flame not proved |
| 56 | PRES_STOF | combustion fan started, but pressure switch stuck off |
| 57 | PRES_STON | combustion fan off, but pressure switch stuck on |
| 58 | PRES_FAIL | With combustion fan running, pressure switch has opened |
| 60 | MOTOR_O-C | Motor open circuit |
| 61 | PUCR_STOF | Power supplied to primary valve control relay, but relay not closing |
| 62 | PUCR_STON | Primary valve control relay closed although no power app |
| 63 | PUCR_FAIL | Primary valve control relay should be closed, but still open |
| 64 | GAS_LKOUT | Gas valve modulating coil exceeding max of 160mA |
| 65 | MTR_LKOUT | While error 30 and 60 is present, motor will lockout |
| 66 | SUCR_STOF | Secondary control relay should be closed but still open |
| 67 | SUCR_STON | Secondary valve control relay closed although no power app |
| 68 | SUCR_FAIL | Secondary control relay should be closed but still open |
| 69 | FUSE_BLOW | 24 volts supply lost as fuse has blown |
| 70 | SS-SDNERR | 2nd micro did not shut down heating cycle |
| 71 | SS-STAERR | Primary micro detected that secondary micro is calling for heat |